PRODUCT  SPECIFICATION

1.PRODUCT  CODE    DPF36702

2. DESCRIPTION           18  Pair  7/.2  (0.2 mm2 )  24AWG  .T.A.C.W.  Polypropylene  insulated.

Aluminium  Laminate  tape  screened.  PVC  sheathed .Data  cable.

RoHS Compliant PVC . Oxygen Free Copper .

3. CONSTRUCTION

3.1  CONDUCTOR :  7  strands  of  0.2 mm  Tinned  Annealed  Copper  to

AS/NZS 1125  drawn  from  Class  102  copper  to  AS1574.

Max.  D.C. resistance  at  20C  :  89  ohms / km

3.2  INSULATION :    Coloured  Data  Grade  Polypropylene.

Nominal  Diameter  :  1.2  mm

Nom.  Wall  Thickness:   0.3   mm

3.3  LAY  UP                18  pre twisted Pairs  laid  up.

Pair1.   Blue   +  White/Blue       	Pair 2.   Orange  +  White/Orange

Pair3    Green +  White/Green	Pair4     Brown   +  White/Brown

Pair5    Grey   +  White/Grey	Pair6     Blue      +   Red/Blue

Pair7    Orange +  Red/Orange	Pair8     Green    +  Red/Green

Pair9    Brown  +  Red/Brown	Pair10   Grey      +  Red/Grey

Pair11  Blue   +  Black/Lt Blue	Pair12   Orange  +  Black/Orange

Pair13  Green +  Black/Green	Pair14   Brown   +  Black/Brown

Pair15  Grey   +  Black/Grey	Pair16   Blue      +  Yellow/Blue

Pair17  Orange +  Yellow/Orange	Pair18   Green    +  Yellow/Green

3.4  SCREEN

Aluminium  /  Polyester  Laminate  tape  in  constant

contact  with  a  7/.2  TACW  drain  wire.

3.4  SHEATH                Coloured  V90  PVC  to  AS/NZS 3808 .

Nominal  Diameter :  12.0    mm

Nom.  Wall  Thickness :   0.76  mm

3.5  TYPICAL  ELECTRICAL

TYPICAL  CAPACITANCE 		     55  pF/m

3.6  PRINTING

At  nominally  1M  spacings  printed  on  sheath :

“TYCAB  AUSTRALIA  MULTIPAIR  DATA  CABLE  ACA N1155 ”