

# PRODUCT SPECIFICATION

1. **PRODUCT CODE** HMC07/2.5
2. **DESCRIPTION** 6 Core + Earth 54/.25 (2.5mmsq). T.C.W. V90HT PVC insulated. White cores numbered V90HT P.V.C. sheathed.

Control cable. 450/750 volt to AS5000.3 Oxygen Free copper. RoHS compliant PVC.

# CONSTRUCTION

* 1. **CONDUCTOR :** 54 strands of 0.25 mm nom. Tinned Annealed Copper to

AS1125 drawn from Class 102 copper to AS1574.

Max. D.C. resistance at 20C : 8 ohms / km

* 1. **INSULATION :** White V90HT PVC to AS3808.

Nominal Diameter: 3.6 mm Nominal Wall Thickness: 0.6 mm

* 1. **LAY UP** 7 Cores laid up

1. White No1 2. White No2 3. White No3 4. White No4 5. White No5 6. White No6 7. Green/Yellow

* 1. **SHEATH** Coloured P.V.C. type V90HT to AS3808

Nominal Diameter: 13.7 mm Nominal Wall Thickness: 1.4 mm

# IDENTIFICATION

Printed on sheath at approx**.** 500mm intervals

TYCAB 7 X 2.5MMSQ 2019 V90HT ELECTRIC CABLE 450/750V