PRODUCT SPECIFICATION

1. PRODUCT CODE	BEM31113

2. DESCRIPTION           	2 Core 1/1.13 + 7/0.4 Earth (1.0mm2 T&E). P.A.C.W.                              		            				V90 Insulated and 3V90 P.V.C. Sheathed.

Flat Twin & Earth Building Cable 450/750 Volt to AS/NZS 5000.2.

Oxygen Free Copper. RoHS Compliant.

TUV AUTHORISED MARKING: TUV022085EA

3. CONSTRUCTION

3.1 CONDUCTOR:   	1 strand of 1.13 mm nom. Plain Annealed Copper to

AS/NZS 1125 Class 2.

Max. D.C. resistance at 20C:	18.1 ohms / km

EARTH:		7 strands of 0.4 mm nom. Plain Annealed Copper to

AS/NZS 1125 Class 2.

Max. D.C. resistance at 20C:	21.2 ohms / km

3.2 INSULATION:    	Coloured V90 P.V.C. to AS/NZS 3808.

Nominal Diameter:  		2.35 mm

Nominal Wall Thickness:   	0.6 mm

Minimum Wall Thickness:	0.44 mm at any point

EARTH:			Nominal Diameter:  		2.35 mm

Minimum Wall Thickness:	0.44 mm at any point

3.3 CORE COLOURS: 	1. RED

2. BLACK

3. LIGHT GREEN/YELLOW (Earth core in the middle of Red & Black core)

Note: EARTH to be 30% min stripe width of Green or Yellow and have

base consisting of Green or Yellow only

Laid parallel

3.4 SHEATH:               	Coloured 3V90 P.V.C. to AS/NZS 3808.

Flat configuration

Nominal Dimensions:    	8.85 x 4.15 mm

Nominal Wall Thickness:    	0.9 mm

Minimum Wall Thickness:	0.67 mm at any point

3.5 IDENTIFICATION:	Printed on the sheath at maximum distance of 550mm:

TYCAB  AUSTRALIA  2017  V90 ELECTRIC CABLE  450/750V TUV022085EA  BEM31113  1MM2  T&E

And Metre Marked